## BladeUPS ROI Comparison
OPERATING COSTS: BladeUPS vs. Other UPS Systems
|  | Load Rating (VA) = | 60000
|  | Load Power Factor = | 1
|  | Unit Watts = | 60000
|  | Energy cost per kW Hr ((usage charge + taxes)/kW/hr) = | 0.0794
|  | Demand charge per kW/hr = | 0.02
|  | Total Cost per kW/hr = | 0.0994 | 48000 | 48000
|  |  |  | 0.44 | 0.44
|  |  |  | 109090.9091 | 21120
|  | Competitive product efficiency from chart = | 91.5%
|  | BladeUPS efficiency from chart = | 97.5%
|  | Loss in watts with competitive product = | 5100
|  | Loss in watts with BladeUPS = | 1500
|  | Extra wattage used to operate competitors product = | 3600
|  | Loss in Btu/hr with competitive product = | 17401.9206
|  | Loss in Btu/hr with BladeUPS = | 5118.2119
|  | Extra Btu/hr used to operate competitors product | 12283.7086
|  | Daily energy savings using BladeUPS = | 8.5882
|  | Yearly energy savings using BladeUPS = | 3134.6784
|  | * Cooling efficiency ratio = | 100%
|  | Daily cooling savings using BladeUPS = | 8.5882
|  | Yearly cooling savings using BladeUPS = | 3134.6784
Total yearly combined savings using BladeUPS = |  |  | 6269.3568
* Cooling efficiency ratio is the ratio of dollars spent to cool IT equipment, when compared to dollars spent to power that same equipment. Most data centers operate their cooling efficiency between 80 to 120%. If you have a highly efficient cooling strategy use 90% or lower. If your cooling strategy is know to be inefficient, use 100% or higher. If you know your actual cooling efficiency input that value.